## 一期
序号 | 项目名称name | 规格型号tpye | 数量quality | 单位 | 备注 | 20251017 TBEA requirements | 20251022 四方前方需要核实
所有测控屏应考虑mimic价格，需用进口品牌； | [6 empty] | mimic屏转换把手需要进口品牌，请前方协助确认转换把手的品牌。 The conversion handle of the mimic panel needs to be of an imported brand. Please assist in confirming the brand of the conversion handle with the on - site team.
CHALINZE 400KV 变电站设备清单 Equipment List of CHALINZE 400kV Substation
4 | 220kV 母线差动保护扩展 220kV Bus Differential Protection Expansion |  | 1 | 套 |  | 原来的母差是NR The original bus differential protection is of the NR brand.
| 母差保护装置 | MiCOM P746 | 3 | 台 |  | 数量没报够，如果新换母差，应包含前期和本期共至少16个间隔双套,是不是至少6台（不同品牌）？ The quantity reported previously was insufficient. If the bus differential protection is newly replaced, it should cover at least 16 bays in double sets for both the previous and current phases. Shouldn't the quantity be at least 6 units (of different brands)? | 母差间隔数需协助核实，特变确认至少16个间隔，能否进一步明确？后期更换为ABB/西门子也需要该信息 The number of bus differential protection bays needs to be verified. TBEA has confirmed at least 16 bays. Can this be further clarified? This information is also required for the later replacement with ABB or Siemens.
| 快速闭锁跳闸继电器 | JFZ-500 | 9 | 个
| 试验底座 | TSB-14 | 5 | 个
| 柜体及相关附件 | 2200mm*800mm*800mm | 1 | 面
本站保护部分少报：Chalinze需要更换2个线路光差，在NR老屏基础上改造 Under - reported protection parts for this substation: Two line optical differential protections in Chalinze need to be replaced, and the modification is based on the old NR panel. | [6 empty] | 请协助询价，询价范围包括南瑞设备，屏柜改造费，调试服务费。可以咨询juma。 Please assist in obtaining quotations, including NARI equipment, panel cabinet modification costs, and commissioning service fees.we can ask juma.
8 | Extend existing Digital Control and Monitoring System to include two 400kV SEGERA line bays and two 220kV BAGAMOYO line bay with all required hardware and software facilities to provide all functional requirements (as per the global standard architecture for Substation Control and Monitoring System) as specified in TS-1 Scope of Supply. |  | 1 | 套 |  | 现有后台是NR，sf测控装置能接入吗？ The existing back - end is of the NR brand. Can the SF control and measurement device be connected? | 1.确认是否可以接入，NR规约是否为61850，如果是，请向当地资源询NR接入费。 2.若不是61850规约，无法接入，则测控屏换成NR，需考虑NR的测控屏设备及服务费。 Confirm whether connection is possible. Check if the NR protocol is IEC 61850. If so, inquire about the NR connection fee from local resources. If it is not the IEC 61850 protocol and connection is not possible, then replace the control and measurement panel with NR, and consider the equipment and service fees for the NR control and measurement panel.
11 | 电能质量监测屏柜Power Quality Monitoring Panel Cabinet | 所有现有及扩建线路及变压器间隔，含屏柜及组屏附件 |  |  |  | 甲供，我司仅提供屏柜及组屏附件
| 屏柜 | 2260:800:600 | 1 | 面 |  | 屏柜数量应按需 | 请提供电能质量数量及尺寸，才能确定所需屏柜数量。Please provide the quantity and dimensions of power quality monitoring equipment to determine the required number of panel cabinets.
Kinyerezi 400/220/33kV变电站及对侧站监控保护系统设备清单
1.16 | 电量质量系统柜Power Quality Monitoring Panel Cabinet | 含组屏附件一套 | 1 | 套 |  | 装置单独招标，我司提供屏柜及附件
| 屏柜panel | 2260:800:600 | 2 | 面 |  | 屏柜数量按需 | 请提供电能质量数量，才能按需配置屏柜。Please provide the quantity and dimensions of power quality monitoring equipment to determine the required number of panel cabinets.
对侧220kV KINYEREZI Ⅰ Substation Opposite - side 220kV KINYEREZI Ⅰ Substation
本站测控原来是ABB的，SF能不能接入？The original control and measurement system of this substation is of the ABB brand. Can the SF system be connected? | [6 empty] | 考虑接入费，核实是否为ABB后台。 1.确认后台品牌及通信规约；规约为61850时，SF测控才可以接入（具体需要和言湘宁确认）； 2.协助询价接入费用； Consider the connection fee and verify whether the back - end is of the ABB brand. Confirm the brand of the back - end and the communication protocol. The SF control and measurement system can only be connected when the protocol is IEC 61850 . Assist in inquiring about the connection fee.
8 | 站内系统接入调试费 | 测控、保护以及计量等相关站内系统接入、扩容调试 | 1 | 套 |  | 母差原来是ABB，新扩2个间隔，需考虑扩容和接入费用 | 协助向ABB询价
7 | 电量质量系统柜Power Quality Monitoring Panel Cabinet | 含组屏附件一套 | 1 | 套 |  | 屏柜数量按需 | 请提供电能质量数量，才能按需配置屏柜Please provide the quantity and dimensions of power quality monitoring equipment to determine the required number of panel cabinets.
对侧220kV KINYEREZI II Substation
本站220线路测控屏2面需要改造，增加Bypass DS Two 220kV line control and measurement panels in this substation need to be modified to add Bypass DS. | [6 empty] | 了解原测控品牌？协助询价改造费用Find out the brand of the original control and measurement system. Assist in inquiring about the modification cost.
1 | 220kV KINYEREZI II 1/2 线路差动保护B | 每面含1台线路差动保护,1台电压切换 | 2 | 面 |  | 按老屏改造4个装置报批，目前报价按4面屏且两套不同品牌。 The approval was made based on modifying 4 devices on the old panel. Currently, the quotation is based on 4 panels with two different brands. | 需了解老屏的品牌，协助询价It is necessary to find out the brand of the old panel and assist in inquiring about the price.
| 线路光差保护装置Line optical differential protection device | CSC-103 | 1 | 台
| 后备过流保护装置Backup over - current protection device | CSC-211 | 1 | 台
| 快速闭锁跳闸继电器Fast - blocking tripping relay | JFZ-500 | 1 | 个
| 快速自复位跳闸继电器Fast self - resetting tripping relay | JFZ-500 | 3 | 个
| 跳闸回路监视继电器 | JFZ-583 | 1 | 个
| 电压切换继电器 | RUS-11B | 1 | 个
| 试验底座 | TSB-14 | 2 | 个
| 柜体及相关附件 | 2200mm*800mm*800mm | 1 | 面
3 | 站内系统接入调试费 In - station System Connection and Commissioning Fee | 测控、保护以、计量等相关站内系统接入、扩容调试 For the connection, expansion, and commissioning of relevant in - station systems such as control and measurement, protection, and metering. | 1 | 套 |  | 现有施耐德后台不在工作状态The existing Schneider back - end is not in working condition. | 1.如果按新上四方后台考虑，仅考虑新上间隔的接入 2.落实业主需求，了解施耐德后台状态 If a new Sifang back - end is considered, only consider the connection of new bays. Implement the owner's requirements and find out the status of the Schneider back - end.
Mkuranga 400/220/33kV变电站及对侧站监控保护系统设备清单
1.16 | 电量质量系统柜Power Quality Monitoring Panel Cabinet | 含1套电能质量采集装置，1套通讯设备。 | 1 | 套 |  | 装置单独招标，我司提供屏柜及附件
| 柜体及相关附件 | 2200mm*800mm*800mm | 2 | 面 |  | 屏柜数量按需 | 请提供电能质量数量及尺寸，才能确定所需屏柜数量Please provide the quantity and dimensions of power quality monitoring equipment to determine the required number of panel cabinets.
Morogoro 220/33/11kV变电站及对侧站监控保护系统设备清单
1.13 | 电量质量系统柜Power Quality Monitoring Panel Cabinet | 含组屏附件一套 | 2 | 面 |  | 装置单独招标，我司提供屏柜及附件
[6 empty] | 屏柜数量按需 | 请提供电能质量数量及尺寸，才能确定所需屏柜数量Please provide the quantity and dimensions of power quality monitoring equipment to determine the required number of panel cabinets.
old Morogoro扩建 | [5 empty] | 少报old Morogoro扩建，换两个老屏的光差，以及后台接入，后台为业主自有品牌 The expansion of old Morogoro was under - reported. Two optical differential protections on old panels need to be replaced, and there is a need for back - end connection. The back - end is of the owner's self - owned brand. | 1.了解业主自有品牌，接入费如何考虑 2.两个老屏的光差，目前方案按主保护ABB/西门子，主二SF考虑 For the two optical differential protections on old panels, the current plan considers ABB or Siemens for the main protection and Sifang for the secondary main protection.